An university-industry driven off-grid solar project for remot
 An university-industry driven off-grid solar project for remote community in Malaysia
Gan Chin Kim, PhD, P.Eng
ckgan@utem.edu.my
Md Nazri Bin Othman, PhD, P.Eng
nazri@utem.edu.my
 EWG 07 2016A Workshop - Off Grid Electrification Option for Remote Regions in APEC
10 September 2018, Chiang Mai, Thailand

---
Presentation Outline
Presentation Outline
Background
Quadruple Helix Model
Project overview
User engagement
Lesson learnt

---
Background
Background
Kampung Tual, Pahang, a 3-hour drive from Kuala Lumpur
Total population of approx. 600 indigenous people
Where
Live without electricity supply
Electricity is needed for children to learn at night and use computers
What
Provide basic electricity supply by installing off-grid solar PV system at a local communal center
Quadruple helix approach
How

---
N 4.150839°
E 101.646849°
N 4.148574°
E 101.648427°
N 4.137780°
E 101.651191°
Corporate Affairs

---
Quadruple Helix Model
Quadruple Helix Model
Pusat Didikan Komuniti / Cenwaey Penaney (NGO)
Samsung Malaysia Electronics
Government
Industry
Academia
Community

---
Project Overview
Project Overview
Kampung Tual
Local communal learning Center
Villages

---
Proposed off-grid solar system
Proposed off-grid solar system
Load	V-system	Watt	Qty	TCL	Runtime	eff	Wh/day
LED light	230	5	30	150	8	0.9	1333
Wall fan	230	50	10	500	6	0.8	3750
LED spot light	230	20	4	80	8	0.9	711
PA system	230	50	1	50	3	0.9	167
Desktop PC	230	100	10	1000	3	0.8	3750
Notebook	230	60	2	120	8	0.8	1200
LCD projector	230	20	1	20	3	0.8	75
4in-1 laser printer	230	200	1	200	2	0.8	500
General IT devices	230	30	10	300	6	0.9	2000
S/S/O	230	300	2	600	1	1.0	600
Subtotal DC-load							0
Subtotal AC-load				3,020W			14,086
Total load							14,086
Estimated energy requirement: 14 kWh / day
Peak Sun Hour (PSH) : 5.0 (Meteonorm database)
Required solar module capacity: 4 kWp
Autonomy day: 3 days

---
Installation
Installation

---
User engagement
User engagement

---
Daily Energy Usage
Daily Energy Usage

---
Needs for remote monitoring
Needs for remote monitoring
Tripping

---
Best Academia-Industry Collaboration Award
Best Academia-Industry Collaboration Award

---
Lesson learnt
Lesson learnt
- Many such projects were awarded mainly based on one-off basic without maintenance contract
- Fit-and-forget approach
- Poor ‘after-sales service’
- Remote system monitoring is a challenge, requires satellite internet connectivity
- Lack of holistic system level network planning, design, operation and maintenance for long term sustainable development

---
Centralized vs Distributed microgrid
Centralized vs Distributed microgrid
Centralized microgrid
Distributed microgrid
AC vs DC microgrid

---
Distributed vs Centralized microgrid
Distributed vs Centralized microgrid

---
Way forward
Way forward
- Development of options portfolio for sustainable rural electrification
- Systems modelling of power systems resilience to natural hazards
- Integrated sustainable and resilient planning under uncertainty considering the role of communities

---
An university-industry driven off-grid solar project for remot (2)
ขอขอบคุณ
THANK YOU
 An university-industry driven off-grid solar project for remote community in Malaysia
Gan Chin Kim, PhD, P.Eng
ckgan@utem.edu.my
Md Nazri Bin Othman, PhD, P.Eng
nazri@utem.edu.my
 EWG 07 2016A Workshop - Off Grid Electrification Option for Remote Regions in APEC
10 September 2018, Chiang Mai, Thailand