Supercapacitor Energy Storage System for PV Power Generation
Supercapacitor Energy Storage System for PV Power Generation
Institute of Electrical Engineering,Chinese Academy of Sciences
Supported by Ministry of Science and Technology,China
May, 2004

---
Applicable  Energy Storage Technology  for PV Power Generation
Applicable Energy Storage Technology for PV Power Generation
The lead-acid battery is popular in PV generation system because of its low cost, but its life cycle is low. Also it will cause environment problem.
Other battery like nickel-metal-hydride battery, Li-ion battery have advantage of high energy density, but they are expansive.
Supercapacitor is becoming an attractive new technology for energy storage.

---
Feature of the Supercapacitor
Feature of the Supercapacitor
Advantages:
- High life cycle (>500000 cycled times)
- Quickly charge/discharge (>1000A)
- Operating temperature range (-50℃-70 ℃ )
- Environment friendly
Limitations:
- Low energy density
- Linear discharge voltage prevents use of the full energy spectrum.
- Cells have low voltages
- High self-discharge

---
The Key Issues for Supercapacitor Energy Storage System
Usually the supercapacitor cell with aqueous electrolyte allows 1V of charge , Whereas organic electrolyte allows 2.5 volts of charge. To operate at higher voltages, supercapacitors are connected in series. On a string of more than three capacitors, voltage balancing is required to prevent any cell from reaching over-voltage.
The gravimetric energy density of the supercapacitor is 1 to 10Wh/kg. Compare to battery, it is lower. Whereas the voltage of the supercapacitor is linear and drops evenly from full voltage to zero volts. Because of this, the supercapacitor is unable to deliver the full charge.

---
In China the supercapacitor as product its technology level:
energy density: about 4Wh/kg
life cycle: 100000-500000 cycled times
operating temperature range (-40℃-70 ℃ )
In order to set up the test system of supercapacitor energy storage, we have investigated two kind supercapacitors from two Chinese companys:
the supercapacitor cell with organic electrolyte:
2700F, 2.7V, 500000 cycled times
the supercapacitor cell with aqueous electrolyte:
20000F, 0.7V, 100000 cycled times

---
1kW PV Power Generation with Supercapacitor Energy Storage（300Wh/2kWh）
PV
Array
Super-
capacitor
Bank
Load
Boost
DC/DC
Converter
Buck
Charger
Energy
Management
And
Control

---
Test System of Supercapacitor Energy Storage (500W/60Wh)
Super-
Capacitor
Bank
AC Power
Supply
Charger
DC/DC
Converter
DC/AC
Inverter
Computer

---
The Picture of the Test System of Supercapacitor Energy Storage (500W/ 60Wh)

---
The supercapacitor bank is consist of 20 cells with organic electrolyte:
2700F,
2.7V,
500000 cycled times
full discharge

---
The Study of Supercapacitor Bank
The Principle of Voltage Balancing for serial connected supercapacitor cells

---
The Principle of exchange between serial and parallel connected for supercapacitor cells

---
The Structure of 60Wh Supercapacitor Bank

---
The result of Voltage Balancing of the Supercapacitor Bank
（Current of Charge：2A Charge duration: 76mintues）
Number of Cells	C1	C2	C3	C4	C5
Voltage of End Charge (V)	2.79	2.77	2.78	2.77	2.82
Number of Cells	C6	C7	C8	C9	C10
Voltage of End Charge(V)	2.78	2.81	2.79	2.79	2.77
Number of Cells	C11	C12	C13	C14	C15
Voltage of End Charge(V)	2.79	2.79	2.77	2.82	2.78
Number of Cells	C16	C17	C18	C19	C20
Voltage of End Charge(V)	2.78	2.78	2.80	2.78	2.77

---
The simulation of Charge and Discharge for 60Wh supercapacitor Bank
（ Current of Charge：1A ，The Load of Discharge is Resistance ）

---
Voltage Wave of Supercapacitor Bank during Charging at Exchange Point from Serial to Parallel Connected
（ Current of Charge： 2A，Tracking Duration ：50s）

---
Voltage Wave of Supercapacitor Bank during Charging at Exchange Point from Serial to Parallel Connected
（ Current of Charge： 2A，Tracking Duration ：500s）

---
The Current and Voltage Wave of Supercapacitor Bank during Charging at Exchange Point from Serial to Parallel Connected
（Constant Load-Computer：200W， Tracking Duration ： 400ms）

---
Study of the Efficiency of Supercapacitor Bank Charging
Supercapacitor by constant voltage charging, the efficiency can be up to 50%
Supercapacitor by constant current charging, the highest efficiency can be gotten。Because of the serial and parallel resistance in Supercapacitor, they will consume electricity when charging. The amount of charging current will affect the charging efficiency.
Many times experiments show that the smaller charging current can lead to higher efficiency.

---
Charging Efficiency under Different Charging Current
(Charging Current from 0.5A to 14A)

---
Study of the Efficiency of Supercapacitor Energy Storage System
Voltage balancing can overcome the problem of the capacitance difference. Each cell can be fully charged.
Through changing from parallel to serial connected, more energy can be output. For example, the supercapacitor bank change from parallel to serial connected for one time while output through DC/DC converter with 1：0.5 input range, the supercapacitor bank can output 93.75% stored energy.
Voltage balancing , changing from parallel to serial connected , high efficiency electronic circuit including charging and discharging converter, The total high efficiency of energy storage can be reached.

---
Summary
This project has already built a test system of supercapacitor energy storage (500W/60Wh), the total efficiency of energy storage is over 60%.
Now the research work is focusing on the development of supercapacitor banks (1kW/300Wh and 1kW/2kWh), energy manager for PV power generation system with supercapacitor energy storage .
In order to increase the energy density of supercapacitor, we are collaborating with the manufacture to increase internal resistance properly for large energy storage usage.