Sustainability of project
WIND TURBINE GENERATION
Research and Development Office
Electricity Generating Authority of Thailand
May 2004

---
Backgrounds
Wind Power Generation Technology
has been introduced in Thailand since
1983.This is mainly attributed to field
test works by Electricity Generating
Authority of Thailand (EGAT).
There are several institutions that
concerning in the field of assessment
wind energy, developing performance
testing and monitoring of wind turbine
for generating electricity.

---
Backgrounds
EGAT has established an experimental
station located in the southernmost of
Phuket Island, near the Andaman Sea.
At this particular site, where is strong
south-west wind from the Andaman -
Sea during monsoon periods, is an ideal
location for WTG experiment.
There are three commercially available
WTG installed; two of 10 kW, Excel from USA and one of 150 kW, from Denmark.

---
Backgrounds
Two of 10 kW are utilized for battery charging station in the year 1993.
The 150 kW WTG was connected to the local distribution grid of PEA
in the year 1996.The 150 kW
WTG was successfully
demonstrated at Promthep
Alternative Energy Station,
Phuket Island with annually
generates 200,000 kWh to
the distribution grid.

---
The annual mean wind speed is varies from 2.5 m/s in the Northern part up to 5.0 m/s in the Southern part of Thailand.
Some specific area of Phuket Island
have been measured and evaluated by EGAT , the result show that the
monthly wind speed is varies from
3.8 to 9.8 m/s
Wind speed and direction
in Thailand
Phuket Island
NE- MONSOON
November-April
SW- MONSOON
May-October

---
Wind Turbine Generation
150 kW
1996
Location of Promthep Alternative Energy Station, Phuket Island

---
AVERAGE WIND SPEEDS (m/s) at 36 m. HEIGHT
PROMTHEP ALTERNATIVE ENERGY STATION, PHUKET PROVINCE
Year	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Average
1994	4.5	4.5	4.7	3.5	6.9	6.1	6.4	5.5	6.0	3.4	3.5	4.4	5.0
1995	5.4	4.9	4.4	3.9	4.3	5.3	4.1	6.1	6.8	4.1	4.9	4.8	4.9
1996	5.0	6.2	4.5	4.0	4.2	3.5	5.8	6.2	7.6	4.3	5.0	4.9	5.1
1997	5.2	4.2	4.4	3.7	5.8	0.0	2.1	7.3	4.0	3.3	4.6	4.9	4.6
1998	5.1	0.0	0.0	0.0	0.0	6.5	4.7	5.8	5.9	6.0	5.1	4.6	5.4
1999	3.8	5.2	4.5	6.3	4.3	9.8	7.6	2.3	0.0	3.9	4.8	4.9	5.2
2000	4.6	0.0	0.0	3.7	3.6	0.0	0.0	0.0	0.0	7.0	4.2	3.3	4.4
2001	4.8	4.7	4.2	3.2	3.9	8.0	6.2	7.8	5.5	4.5	4.3	4.1	5.1
2002	4.4	5.5	4.6	3.8	4.5	4.3	5.0	5.2	6.2	4.2	3.2	4.5	4.6
2003	4.9	5.0	5.0	4.2	6.0	4.0	5.7	6.0	6.8	5.5	4.0	4.7	5.2
Average	4.8	5.0	4.5	4.0	4.8	5.9	5.3	5.8	6.1	4.6	4.4	4.5
Monthly mean wind speed (m/s) in Phuket Island

---
The annual energy supply to the distribution grid.
Energy Production form WTG 150kW.(1996-2004)
	1996	1997	1998	1999	2000	2001	2002	2003	2004
Jan	0	19,195	18,911	8,454	** 0	10,002	32,946	20,148	35,136
Feb	0	10,147	14,620	16,464	6,504	** 234	18,942	18,012	15,036
Mar	0	6,653	13,176	14,724	4,242	12,330	11,376	12,594	15,762
Apr	0	5,202	12,080	26,076	1,284	10,608	5,628	4,704
May	0	22,814	4,090	4,656	** 0	26,556	15,792	21,636
Jun	0	13,371	23,506	7,728	48,942	30,426	8,820	3,636
Jul	* 29,010	12,119	19,107	46,020	23,106	24,162	21,126	11,826
Aug	14,034	35,976	8,944	33,828	21,846	50,184	28,914	26,172
Sep	38,634	11,965	18,354	15,618	12,708	** 4,602	4,854	36,780
Oct	14,243	5,980	29,868	21,804	37,842	13,626	** 48	15,366
Nov	15,109	11,145	16,972	11,130	7,284	20,040	** 2,934	4,314
Dec	11,483	16,974	13,817	** 996	6,342	13,626	6,288	17,718
Total	122,513	171,541	193,445	207,498	170,100	216,396	157,668	192,906	65,934
Electrical Energy
= 195000-210000 kWh/yr
= 1300 -1400 kWh/kW/yr

---
Conceptual Design
The requirement of any WTG
are :
Low investment cost,
Long life under vigorous
climatic conditions
Automatically operation
Low maintenance cost.

---
Sustainability of project
    150 kW WTG Project will be sustained, according to:
    - Reliability of the system
    - Capability of technicians
    - Operation and maintenance can be done well
    - Financial for operation and maintenance available
    - The project give benefit to the community, and
    - The community accept WTG technology

---
Community/People Participation
This project was installed and requested the permission from a
governor of Phuket Island and other authorities.
At the same time, we provide information of WTG to a group of
people in local area. They know and accept a new technology in
their area.
It is very successful to convince the people in the local area to
believe in WTG technology that not impact to their life.

---
Benefit to user and community
- To be proud that they had a new technology in their areas
- Implant mind of conservative energy by saving and reducing energy consumption
- To be a sight seeing or learning by any people who interest in this technology
- The site is on the highest hill so this place is the visiting point of a tourist for seeing view of WTG.
- Improving their knowledge, and skills especially in WTG technical aspects.
- Good health by good environment

---
Maintenance Scheme
- During the installation, the contractor conducted the training for technicians. Contractor also gave the manual of operating instructions, and the guidelines of maintenance.
- After that the EGAT’s technicians can operate and maintain the WTG by themselves.
- In each year, we have a schedule of maintenance for preventive maintenance and get high performance.
- We take one week for yearly maintenance. The time for maintenance will be conducted in November because of the minimum wind speed in each year.

---
Maintenance Scheme
- Since the 150 kW wind turbine was established in 1996 until the present, the WTG technology for grid connected is found that it is easily to operate and has the low cost in maintenance.
- This demonstration is shown to other authority so they have planned to set it up WTG in their local area.

---
Life of System
How to maintain the life of WTG
- The WTG life is 20 years estimated. From our experience, we can do it better maintenance and its life will be increase more than 20 years.
- The past recordations of the operated WTG were the wind velocity, the performance and electric energy. We can be used the data for research and development including the maintenance for example; it will use for education and training to the other countries in Asian country.

---
Cost Effectiveness
- The cost of generating electricity from WTG is 5.02 Baths per unit which is 50% less expensive than the cost of generating electricity from the solar cell.
- In case of commercial scale, the energy cost of established the large WTG, which is more than 600kW, is reduced more than 50% compare to the energy cost from 150 kW WTG.
- EGAT plans to establish a new wind turbine project which the power generated is more than 600 kW in the future.

---
N
10 kW WTG
150 kW WTG
600 kW WTG
10 kW WTG

---
Conclusion
Total Investment Cost
WTG	=	1.25-1.50 US$/Watt
Annual Electrical Energy Generated
WTG	=	1,300-1,400 kWh/kW/yr
Cost of Generation (without grant)
WTG	=	3.5-4.0 Baht/kWh