Appropriate Technology
for
Solar Tracking System
Mr.Pinij Siripuekpong
Assistant Director of
Research and Development Office
Electricity Generating Authority of Thailand

---
Outline
- Background
- The Principle of Solar Tracking System
- Design and components
- Testing
- Conclusion

---
Background
PV solar water pumping system will be started
at 9:30 and stopped at 15:00
The most simple and principal way to get more
energy output from the PV modules is rotating
the modules following the sun as it orbits from
the East to the West during the day.
The problems of solar tracking system are :-
* Imported tracking system (high investment cost)
* No spare parts for maintenance
* high energy consumption for tracking system

---
The amount of electrical energy generated from PV panels
depends on incident angles/projected areas
Projected Area
Collector Area
PV panels

---
Comparison of Solar Energy (Stationary vs. Tracked)

---
Photovoltaic Solar Water Pump
PV Solar Panels
Storage Tank
Filter Tank
Controller
Water Pipe line

---
Cumulative PV Installation in Thailand
(2001)
Applications Peak kW installed
- Water pumping 1061.3
- Stand alone for home village 195.3
- Battery charging station 1821.3
- Telecommunication repeater 1,513.0
- Remote primary school 165.0
- Remote health care 21.0
- Navigation aid 18.0
- Hybrid/Grid Interface 247.3
- Miscellaneous 123.3
Total 5,165.5
[Speaker Notes: Before we move to the third part for Future project, I want you to know 1999’s record of the cumulative PV installation in Thailand by the sector of application. Applications Peak kW installed - Water pumping 892.00 - Stand alone for home village 185.00 - Battery charging station 1,520.00 - Telecommunication repeater 1,513.00 - Remote primary school 65.00 - Remote health care 21.00 - Navigation aid 18.00 - Hybrid/Grid Interface 130.26 - Miscellaneous 98.00 Total 4,442.26]

---
Objectives
The Design of Solar Tracking System for PV water
pumping system aims to
-: Get more volume of water/Day
-: Use local materials
-: Lower maintenance and system cost
-: Get more reliability & better performance from
PV system than stationary one used

---
The Principle of Solar Tracking System
Take Moment / Consider about Center of Gravity
Fulcrum
Water
w4
G
w2
wR
w3
w1
size 12{W rSub { size 8{R} } = Sum cSub { size 8{i=1} } cSup { size 8{n} } {W} } {}
size 12{ {overline {x}} = { { Sum cSub { size 8{i=1} } cSup { size 8{n} } {x rSub { size 8{i} } W rSub { size 8{i} } } } over {W rSub { size 8{R} } } } , {overline {y}} = { { Sum cSub { size 8{i=1} } cSup { size 8{n} } {y rSub { size 8{i} } W rSub { size 8{i} } } } over {W rSub { size 8{R} } } } , {overline {z}} = { { Sum cSub { size 8{i=1} } cSup { size 8{n} } {z rSub { size 8{i} } W rSub { size 8{i} } } } over {W rSub { size 8{R} } } } } {}
size 12{ {overline {x}} = { { Sum cSub { size 8{i=1} } cSup { size 8{n} } {x rSub { size 8{i} } W rSub { size 8{i} } } } over {W rSub { size 8{R} } } } =0} {}
x
y
z


---
Conceptual Design of Solar Tracking System
1. Single axis Solar Tracking System (E-W tracking direction)
- Solar Tracking has been installed in N-S axis,
- Tilt angle 15o (facing South)
2. The basic principle to follow the Sun is by transfering a water
to one side and drain off another side
- by using 2 pipes for counter weight and water from storage tank
3. Use sensors and controllers for controlling pumps automatically
- 4 LED are used as a sensor of the sun direction which create signals
to control valves.
- Limit switches are used to limit the end position of solar tracking
system when the sun orbits out of the limit position in the morning
and evening (Left&Right)

---
Component of 450 Wp Solar Tracking System
for Solar Home
Small Pump
Small Pump

---
Component of 1.05 kWp Solar Tracking System
for PV Water Pumping
Sensor and controller
Control Valves
PVC pipe
Control Valves

---
4
3
2
1
E
W
E
W
4
3
2
1
A
B
E
W
4
3
2
1
A
B
E
W
4
3
2
1
A
C
The Principle Sensor for Tracking System
E
W
4
3
2
1
A
C
Case: Reversing
Case: Tracking Sun

---
Details of Solar Tracking System 1
6 PV panels = 6 x 75 Wp
= 450 Wp
Sensor&Controller
Stationary Solar Cells
Solar Tracking Solar Cells
Water Pump
Load & Data Logger

---
Details of Solar Tracking System 2
PV panels = 14 x 75 Wp
= 1050 Wp
Sensor&Controller
Stationary Solar Cells
Solar Tracking Solar Cells
Control Valve
Load & Data Logger

---
Energy Output & Solar Radiation
Tracking vs. Non-Tracking
29 November 2003
-
100.00
200.00
300.00
400.00
500.00
600.00
700.00
800.00
900.00
1,000.00
600
800
1000
1200
1400
1600
1800
Solar Radiation (W/m
2
)
-
50.00
100.00
150.00
200.00
250.00
300.00
350.00
400.00
450.00
500.00
Power (W)
Solar Radiation : Non Tracking
Solar Radiation : Tracking
Power : Non Tracking
Power : Tracking
Solar Radiation : Non-Tracking 6,010.97 Wh/m
2
/Day
Tracking 7,223.45 Wh/m
2
/Day
% Increase 20.17%
Energy : Non-Tracking 2,015.54 Wh/Day
Tracking 2,549.37 Wh/Day
% Increase 26.49%

---
Variation of Energy Output
Tracking vs. Non-Tracking
DATA : NOVEMBER 2003
Solar Cell : Shell Solar
6 panels/Set, 75 Watts/panel

---
Compared Solar Radiation
Non-tracking/Tracking System
Second Model
First Model

---
Compared PV Energy from
Non-tracking/Tracking System
Increase 20.99%
Increase 23.29%
Increase 20.30%
Second Model
Increase 20.64%
First Model

---
System cost for Solar Home
450 Wp of Solar Cells (75 Wp: 6 panels) / 1 solar Tracker set
2. The net electrical energy output is increased ~ 20% higher than
Non-tracking system
3. In reverse, the installation of PV module less to 90 Watt peak,
which cost about 360 US$ can generate the same amount
of electric energy.
4. The cost of tracking system is 120 US$/unit, so EGAT can
save 200 US$/set

---
System cost for Solar Pump
1050 Wp of Solar Cells (75 Wp: 14 panels) / 1 solar Tracker set
2. The net electrical energy output is increased ~ 20% higher than
Non-tracking system
3. In reverse, the installation of PV module less to 210 Watt peak,
which cost about 840 US$ can generate the same amount
of electric energy.
4. The cost of tracking system is 500 US$/unit, so EGAT can
save 340 US$/set

---
Conclusion
The invention of Solar Tracking System helps us improve
the performance of PV solar system in a simple way
we can build the Solar Tracking System easily with cost
effectiveness for the maximum energy or water output from
any kind of PV Solar Home or Solar Water Pumping