EPPO
EGAT
Mae Hong Son PV Project
Research and Development Office
Electricity Generating Authority of Thailand
May 2004

---
Outline
- Introduction
- Existing power supply and demand
- Scope of works
- Specifications
- System Operation
- Benefit of project

---
Introduction of Mae Hong Son PV Project
- Area 12,681 km2. (1,268,100 acre)
- Mountain and forest ~ 78% of total area
- 9 National forest reserves
- 7 Permanent forest boundaries
- 4 Wild life sanctuaries
- 3 National parks
- 3 Forest parks
- 4 Arboretums
- Population 230,000 (in 1997)
[Speaker Notes: I want you to know the outline of Mae Hong Son area. :- This area consists of forests and hilly mountains and there are many national parks. :- Power supply in this area comes from small hydro power and diesel power stations as the self- sufficient style.]

---
Outline of Power Supply
Mae Hong Son is the only one province where electricity can not be directly transferred from EGAT HV transmission lines (115 kV) , except PEA's distribution lines (22 kV)
EGAT’s plan of 115 kV transmission lines was terminated because of forest reservation reason
The power plants are rather small so electricity supply will be less than the future demand
Mae Hong Son is the forest reservation area for the main purpose of tourism
EGAT installed 6 units of 1,000 kW Diesel Power Plants to support the demand in this area

---
Outline of Power Demand
:- Power Demand in the future will increase at the rate of 6-8 %
per year.
:- In 1998/1999 the Japan International Cooperation Agency
(JICA) provided EGAT with their experts to process the FS
of PV Power in Mae Hong Son province.
:- As a result of all above, EGAT’s plan to build PV power plants
of 500 kW and 1.75 MW in Muang District (1st Phase).

---
Mae Hong Son
Distribution Line
Map
Province
District
Village
Diesel power plant
22 kV distribution line
Dam
N

---
Power Plant in Mae Hong Son Area
Existing Power Supply and Demand
Demand Peak Off Peak
Zone A :- Hydro Plant 4,700 kWp. 6.38 MW. 3.83 MW.
Diesel Plant 5,400 kWp.
Zone B :- Hydro Plant 1,500 kWp. 5.47 MW. 2.84 MW.
Diesel Plant 2,700 kWp.
22 kV line
Zone C :- Hydro Plant 2,100 kWp. 2.77 MW. 1.65 MW.
22 kV line

---
The Site and Capacity of PV Power Plant
in Mae Hong Son
Zone A :- Mae Hong Son-1 Capacity 1,750 kWp.
Mae Hong Son-2 Capacity 500 kWp.
Zone B :- Mae Sariang Capacity 1,000 kWp.
Khun Yuam Capacity 250 kWp.
Zone C :- Pang Ma Pha Capacity 250 kWp.
Khun Yuam Capacity 500 kWp.

---
500 kW PV Power Station in Mae Hong Son -2

---
Solar Cell ASE-300-DG-FT Module
Power (max.) 300 Wp x 1680 Modules

---
Wiring and Data Collection

---
Electrical Control Room

---
Control Room
Invertors Room
Electrical Room

---
Battery Room
1,200 AH 560 V

---
AC Battery
200 kW x 2 sets of
Converter
Power Conditioning Units
250 kW x 2 sets

---
PV Efficiency on DC side (7 April 2004)

---
PV Efficiency on AC side (7 April 2004)

---
PV ARRAY
504 kWp
500 kWp PV POWER PLANT DIAGRAM
BATTERY BANK
560 V, 900 Ah
450-700 Vdc
INVERTER
200 kVA x 2
SYSTEM MONITOR
CONTROLLER AND
DATA ACQUISITION
INVERTER
250 kVA x 2
SYSTEM
CONTROLLER
SWITCH GEAR
22 kV
22 kV
400 Vac 3 D
INDOOR TRANSFORMER
630 kVA
PEA GRID SYSYEM
22 kV 3 Y

---
System Cost
The investmant cost of 500 kW. PV power plant are
from EGAT own budget (13.25%) and
from Energy Conservation Promotion Fund,
Energy Planning and Policy Office (86.75%).
EPPO	=	3.831 MUS$	= 86.75 %
EGAT	=	0.585 MUS$	= 13.25 %
Total Cost	=	4.416 MUS$	= 100.00 %

---
System Operation
1. Sunlight incident on PV modules
Solar Energy --> DC current --> Controller
--> Inverter (with MPPT)
2. Inverter change DC current --> AC current -->
Transformer --> Switch Gear --> PEA
3. Short time of clouding period --> capacity will decrease so
that electricity from batteries will be added
4. PV power plant will generate in daytime.
After that, Mae Sa Nga power plant will save water which
stored in daytime to produce electricity during evening peak.

---
Benefit of MHS Project
Energy Reservation
- Generation from PV	: 700,000	kWh/year
- Decrease in diesel oil	: 215,385	Litre/year
Environmental Reservation
Source of energy from the sun is a clean energy
Decrease in burning of diesel oil and
Reduce greenhouse gas (CO2) : 520.10	Ton/year

---
CONCLUSION
Most PV projects in Thailand are independently conducted by
government organizations which depend on their functional
responsibilities
PV technology for grid support is important in remote
applications.
If the PV price continues to drop, PV’s efficiency increases
and the energy situation, environmental impact cause more
concern, the widespread use of PV Power Plant may become
feasible by the next decade.