## Slide 1
TWO SOLAR PROJECTS:
RURAL AND URBAN AUSTRALIA
Energy and Environment Division
Department of Industry, Tourism and Resources
EGNRET 23, Christchurch NZ
10-13 November 2004

## Slide 2: Presentation Overview
Anangu Pitjantjatjara Solar Station, rural South Australia—a unique 220KW power station concentrating energy before conversion
Kogarah Town Square, Sydney—a redeveloped roof integrated PV station

## Slide 3
Anangu Pitjantjatjara Solar Station
Area covers 100,000 sq km with a population of 2,500
Power Station consists of 10 CS500 connected to a mini-grid servicing a number of communities

## Slide 4
uses Solar System’s high concentration PV technology with mirrored parabolic collectors to concentrate the sun approx. 500 times onto PV receivers
has approx. 130 sq.m. of curved mirrors and its own control system and inverter
tracks the sun on dual axes from sunrise to sunset, maximising output
has the potential to upgrade by replacing the receiver with higher-efficiency PV modules
Each CS500 dish
TECHNOLOGY

## Slide 5
focuses the sunlight to the cell bank in the receiver, where it is converted immediately to DC electricity
- a matched inverter then produces 22kWe of standard 3 phase, 415 Volt AC power at output terminals
- a fan-forced heat exchanger cools the solar cell receiver
is capable of operating independently from the rest of the power station

## Slide 6
The Solar Power Station
includes an on-site control room but may be fully monitored and operated from a distance, vital when working in very remote areas
will complement a 3MW diesel station, reducing diesel consumption by an anticipated 160,000 litres a year, with significant financial and GHG savings
is expected to produce approx. 0.5 GWh of electricity a year
with the modular nature of the CS500 dish, is capable of being sized up or down, according to community needs

## Slide 7
Kogarah Town Square PV Power Station
Australia’s largest, solar-powered, medium-density residential and commercial development
includes a roof integrated PV power station designed by EnergyAustralia

## Slide 8
2800 m2 PV modules placed on all roof surfaces rather than just north-facing ones
- a Solardek system used for main part of the roof, utilising Uni-Solar PV laminates which perform well in hot weather - transparent glass PV modules placed on an awning and a glass roof in the building
will incorporate at least 160kW of modular PV solar capacity

## Slide 9
connected to the electricity grid via 58 computer-monitored Sunpower inverters,
- enabling energy produced to be displayed locally and over the internet
excess energy to be exported to the grid
expected to generate 153,000 kWh a year, with greenhouse gas savings of 140 tonnes